## Export Summary
This document was exported from Numbers. Each table was converted to an Excel worksheet. All other objects on each Numbers sheet were placed on separate worksheets. Please be aware that formula calculations may differ in Excel.
Numbers Sheet Name | Numbers Table Name | Excel Worksheet Name
Data
| Table 1 | Data
Model036FullLoad
| Table 1 | Model036FullLoad
Flow 12
| Table 1 | Flow 12

## Data
EWT | Flow | PSI | FT | HC | Heating Power | HE | LAT | COP | TC | SC | S/T | Cooling Power | HR | EER
20 | 6 | 1.24 | 2.87
20 | 9 | 1.99 | 4.59
20 | 12 | 3.39 | 7.82 | 12.73 | 0.94 | 9.45 | 78.4 | 3.97
30 | 6 | 1.13 | 2.61
30 | 9 | 1.8 | 4.16 | 13.67 | 0.94 | 10.24 | 79 | 4.27 | 22.47 | 18.48 | 0.82 | 0.32 | 23.6 | 71
30 | 12 | 3.2 | 7.39 | 13.88 | 0.95 | 10.4 | 79.2 | 4.28 | 22.7 | 18.67 | 0.82 | 0.3 | 23.7 | 75.7
40 | 6 | 1.02 | 2.35 |  |  |  | 20.8
40 | 9 | 1.61 | 3.73 | 16.35 | 0.96 | 12.9 | 81 | 5 | 21.79 | 19.79 | 0.91 | 0.45 | 23.3 | 48
40 | 12 | 3.01 | 6.96 | 16.6 | 0.97 | 13.1 |  | 5.01 | 22.02 | 19.99 | 0.91 | 0.43 | 23.5 | 51.2
50 | 6 | 0.9 | 2.09 | 17.73 | 0.96 | 15.31 | 82.4 | 5.75 | 21.7 | 19.5 | 0.9 | 0.42 | 23.8 | 51.3
50 | 9 | 1.43 | 3.29 | 19.02 | 0.97 | 15.56 | 82.6 | 5.76 | 21.86 | 19.9 | 0.91 | 0.39 | 23.8 | 56
50 | 12 | 2.83 | 6.53 | 19.31 | 0.98 | 15.81 | 82.8 | 5.78 | 22.08 | 20.1 | 0.91 | 0.37 | 23.9 | 59.7
60 | 6 | 0.79 | 1.82 | 21.18 | 0.97 | 17.72 | 84 | 6.37 | 23.26 | 21.68 | 0.93 | 0.44 | 25.7 | 52.4
60 | 9 | 1.24 | 2.86 | 21.51 | 0.99 | 18 | 84.2 | 6.38 | 23.57 | 22.02 | 0.93 | 0.42 | 25.9 | 55.6
60 | 12 | 2.64 | 6.1 | 21.84 | 1 | 18.28 | 84.4 | 6.4 | 23.98 | 22.47 | 0.94 | 0.41 | 26.2 | 58.5
70 | 6 | 0.68 | 1.56 | 23.64 | 0.98 | 20.11 | 85.6 | 7.03 | 21.89 | 20.61 | 0.94 | 0.58 | 24.9 | 37.4
70 | 9 | 1.05 | 2.43 | 24 | 1 | 20.43 | 85.9 | 7.05 | 22.23 | 20.93 | 0.94 | 0.56 | 25.1 | 29.8
70 | 12 | 2.45 | 5.67 | 24.37 | 1.01 | 20.75 | 86.1 | 7.07 | 22.69 | 21.35 | 0.94 | 0.54 | 25.4 | 42
80 | 6 | 0.56 | 1.3 | 25.64 | 1 | 22.06 | 87 | 7.48 | 20.51 | 19.6 | 0.96 | 0.74 | 24.1 | 27.8
80 | 9 | 0.87 | 2 | 26.04 | 1.02 | 22.41 | 87.2 | 7.5 | 20.83 | 19.91 | 0.96 | 0.7 | 24.2 | 29.7
80 | 12 | 2.27 | 5.23 | 26.43 | 1.03 | 22.76 | 87.5 | 7.52 | 21.26 | 20.32 | 0.96 | 0.68 | 24.6 | 31.3
90 | 6 | 0.45 | 1.04 | 27.65 | 1.01 | 24.01 | 88.3 | 7.99 | 18.92 | 18.03 | 0.95 | 0.88 | 23.1 | 21.6
90 | 9 | 0.65 | 1.57 | 28.07 | 1.03 | 24.39 | 88.6 | 8.01 | 19.21 | 18.31 | 0.95 | 0.84 | 23.2 | 23
90 | 12 | 2.08 | 4.8 | 28.5 | 1.04 | 24.77 | 88.8 | 8.03 | 19.61 | 18.69 | 0.95 | 0.81 | 23.5 | 24.2
100 | 6 | 0.34 | 0.78
100 | 9 | 0.49 | 1.14 | [5 empty] | 18.33 | 17.49 | 0.95 | 0.98 | 22.9 | 18.7
100 | 12 | 1.89 | 4.37 | [5 empty] | 18.61 | 17.84 | 0.96 | 0.95 | 23.1 | 19.6
110 | 6 | 0.22 | 0.51
110 | 9 | 0.31 | 0.71 | [5 empty] | 17.34 | 16.66 | 0.96 | 1.12 | 22.5 | 15.5
110 | 12 | 1.71 | 3.94 | [5 empty] | 17.61 | 17 | 0.97 | 1.09 | 22.6 | 16.2
120 | 6 | 0.11 | 0.25
120 | 9 | 0.12 | 0.27 | [5 empty] | 16.06 | 15.98 | 0.98 | 1.26 | 21.7 | 12.8
120 | 12 | 1.52 | 3.51 | [5 empty] | 16.3 | 16 | 0.98 | 1.22 | 21.8 | 13.4

## Model036FullLoad
Table 1
EWT | Flow | PSI | FT | HC(MBtu/hr) | Heating Power(kW) | HE | LAT | COP | TC | SC | S/T | Cooling Power (kW) | HR(MBtu/hr) | EER
20 | 9 | 3.17 | 7.32 | 22 | 1.78 | 18.3 | 86.5 | 3.62
30 | 9 | 3 | 6.93 | 27 | 2.11 | 22.9 | 90.5 | 3.75 | 48.9 | 35.5 | 0.72597 | 1.26 | 47.9 | 38.8095
40 | 9 | 2.83 | 6.54 | 32 | 2.35 | 26.4 | 93.2 | 3.99 | 46.9 | 34.3 | 0.73134 | 1.33 | 49.5 | 35.2632
50 | 9 | 2.67 | 6.16 | 37 | 2.49 | 30 | 95.9 | 4.35 | 44.8 | 33 | 0.73661 | 1.43 | 51.1 | 31.3287
60 | 9 | 2.5 | 5.77 | 42 | 2.54 | 34.7 | 99.4 | 4.85 | 42.7 | 31.5 | 0.7377 | 1.55 | 50.8 | 27.5484
70 | 9 | 2.33 | 5.39 | 47 | 2.53 | 39.4 | 102.9 | 5.44 | 40.7 | 29.4 | 0.72236 | 1.71 | 50 | 23.8012
80 | 9 | 2.17 | 5 | 47 | 2.53 | 39.4 | 102.9 | 5.44 | 38.6 | 29 | 0.7513 | 1.93 | 48.7 | 20
90 | 9 | 2 | 4.62 | 47 | 2.53 | 39.4 | 102.9 | 5.44 | 36.5 | 28.6 | 0.78356 | 2.26 | 46.9 | 16.1504
100 | 9 | 1.83 | 4.23 | [5 empty] | 34.5 | 28 | 0.81159 | 2.78 | 46.6 | 12.4101
110 | 9 | 1.66 | 3.85 | [5 empty] | 35.1 | 29.7 | 0.84615 | 3.3 | 46.4 | 10.6364
120 | 9 | 1.5 | 3.46 | [5 empty] | 33.2 | 28.9 | 0.87048 | 3.65 | 45.6 | 9.0959

## Flow 12
EWT | Flow | PSI | FT | HC | Heating Power | HE | LAT | COP | TC | SC | S/T | Cooling Power | HR | EER
20 | 12 | 3.39 | 7.82 | 12.73 | 0.94 | 9.45 | 78.4 | 3.97
30 | 12 | 3.2 | 7.39 | 13.88 | 0.95 | 10.4 | 79.2 | 4.28 | 22.7 | 18.67 | 0.82 | 0.3 | 23.7 | 75.7
40 | 12 | 3.01 | 6.96 | 16.6 | 0.97 | 13.1 |  | 5.01 | 22.02 | 19.99 | 0.91 | 0.43 | 23.5 | 51.2
50 | 12 | 2.83 | 6.53 | 19.31 | 0.98 | 15.81 | 82.8 | 5.78 | 22.08 | 20.1 | 0.91 | 0.37 | 23.9 | 59.7
60 | 12 | 2.64 | 6.1 | 21.84 | 1 | 18.28 | 84.4 | 6.4 | 23.98 | 22.47 | 0.94 | 0.41 | 26.2 | 58.5
70 | 12 | 2.45 | 5.67 | 24.37 | 1.01 | 20.75 | 86.1 | 7.07 | 22.69 | 21.35 | 0.94 | 0.54 | 25.4 | 42
80 | 12 | 2.27 | 5.23 | 26.43 | 1.03 | 22.76 | 87.5 | 7.52 | 21.26 | 20.32 | 0.96 | 0.68 | 24.6 | 31.3
90 | 12 | 2.08 | 4.8 | 28.5 | 1.04 | 24.77 | 88.8 | 8.03 | 19.61 | 18.69 | 0.95 | 0.81 | 23.5 | 24.2
100 | 12 | 1.89 | 4.37 | [5 empty] | 18.61 | 17.84 | 0.96 | 0.95 | 23.1 | 19.6
110 | 12 | 1.71 | 3.94 | [5 empty] | 17.61 | 17 | 0.97 | 1.09 | 22.6 | 16.2
120 | 12 | 1.52 | 3.51 | [5 empty] | 16.3 | 16 | 0.98 | 1.22 | 21.8 | 13.4

## Model72 - Flow 18
Versatec VS Heat Pump Model 072 - Full Load assuming the HP flow rate at 18 gpm
EWT | Flow | PSI | FT | HC | Heating Power | HE | LAT | COP | TC | SC | S/T | Cooling Power | HR | EER
30 | 18 | 6 | 13.86 | 53.9 | 4.87 | 45 | 97.2 | 3.24 | 78.2 | 51.5 | 0.66 | 2.47 | 89 | 31.7
40 | 18 | 5.81 | 13.43 | 62.5 | 5.07 | 50.3 | 100.1 | 3.62 | 79.2 | 51.9 | 0.66 | 2.94 | 91.6 | 26.9
50 | 18 | 5.63 | 13 | 71.1 | 5.28 | 55.7 | 103 | 3.95 | 80.1 | 52.3 | 0.65 | 3.43 | 94.2 | 23.4
60 | 18 | 5.44 | 12.57 | 79.8 | 5.47 | 68.6 | 109.6 | 4.27 | 77.8 | 51.3 | 0.66 | 3.83 | 92.9 | 20.3
70 | 18 | 5.25 | 12.13 | 88.4 | 5.67 | 71.6 | 111.5 | 4.57 | 75.5 | 50.5 | 0.67 | 4.31 | 91.4 | 17.5
80 | 18 | 5.07 | 11.7 | 97 | 5.88 | 75.8 | 113.8 | 4.84 | 73.7 | 49.8 | 0.68 | 4.78 | 90.6 | 15.4
90 | 18 | 4.88 | 11.27 | 105.6 | 6.08 | 80 | 116.1 | 5.09 | 68.3 | 49 | 0.72 | 5.17 | 85.9 | 13.2
100 | 18 | 4.69 | 10.84 | NAN | NAN | NAN | NAN | NAN | 63.8 | 47.5 | 0.74 | 5.75 | 83.4 | 11.1
110 | 18 | 4.51 | 10.41 | NAN | NAN | NAN | NAN | NAN | 57.1 | 44.1 | 0.77 | 6.68 | 79.9 | 8.5
120 | 18 | 4.32 | 9.98 | NAN | NAN | NAN | NAN | NAN | 50.3 | 41.3 | 0.82 | 7.68 | 76.5 | 6.5